Utility Cluster’s Proposed Interconnection Standards Process

Based on the Discussion in the 11.12 Working group meeting

Includes DGC Response (2002_1119,6:00pm).

Figure 2 (revised)  is a flow chart showing an expedited interconnection process based upon California PUC Rule 21, IEEE standards and material from Attachment A of the current FERC ANOPR negotiations. It also introduces the concepts of a Simplified Interconnection and an Expedited Interconnection which are discussed further in the following Notes indicated on Figure 2.

(Specific responses in bold italics.  Also, reformated lists in Notes for clarity)

# Figure 2 (revised): Proposed Process for Expedited DG Interconnection

(Basis documents: CA Rule 21, IEEE Standards, FERC ANOPR-Att. A)

Note 1.  “This screen only applies to Generating Facilities that start by motoring the Generating Unit(s)”, from California PUC Rule 21. Refer to this document, Sheet 30, for further information.

Note 2.  The purpose of this screen is to ensure that fault (short-circuit) current contributions from all DG units will have no significant impact on the Company’s [Interconnection Provider’s] protective devices and system. Refer to California PUC Rule 21, Sheets 31-32, for further information and relevant material from FERC ANOPR Attachment A.  Coordination of fault-current protection devices and systems will also be examined as part of this screen.

Note 3.  This screen includes a review of the type of electrical service provided to the customer Facility, including line configuration (see California PUC Rule 21, Sheet 32) and the transformer connection.  The following is from current consensus language in Attachment A of the FERC ANOPR process, relating to generators up to 2 MW.  “If the proposed generator is to be interconnected on a single-phase transformer shared secondary, the aggregate generation capacity on the shared secondary, including the proposed generator, will not exceed 20 kVA.”  Further, item 10 of this document states “If the proposed generator is single-phase and is to be interconnected on a center tap neutral of a 240 volt service, its addition will not create an imbalance between the two sides of the 240 volt service of more than 20% of nameplate rating of the service transformer.”

Note 4.  The following is from current consensus language in Attachment A of the FERC ANOPR process.  “The proposed generator, in aggregate with other generation interconnected to the distribution low voltage side of the substation transformer feeding the distribution circuit where the generator proposes to interconnect, will not exceed 10 MW in an area where there are known or posted transient stability limitations to generating units located in the general electrical vicinity (e.g., 3 or 4 transmission voltage level buses from the point of interconnection).”

Note 5. TOTALLY NEW MATERIAL   For Category 1 customers [Facilities] (10 kW or less) [and those that meet the prescribed screens], the Notice of Intent to Interconnect form (modified appropriately) will serve as Notice, Application and Interconnection Agreement (contract).  This new Simplified Interconnection  process has four steps:

- [Interconnection] Customer submits form filled out properly and completely (perhaps with help from the Company [Interconnection Provider])

- Company [Interconnection Provider] verifies Facility equipment complies with UL 1741 and IEEE 929-2000 (as appropriate);

- Company [Interconnection Provider] inspects completed installation for compliance with standards

- Assuming inspection is satisfactory, Company [Interconnection Provider] notifies [Interconnection] Customer that interconnection is allowed and notifies Company [Interconnection Provider]) departments as shown in Figure 1.

Note 6.  TOTALLY NEW MATERIAL  Incorporating aspects of the screening process adopted by several states, the Company [Interconnection Provider] is proposing a new Expedited Interconnection process for Facilities that pass all the [prescribed] screens shown above.  It is expected that the level of effort will range from 2 to 20 professional-level hours for the Company [Interconnection Provider] to apply these screens, with cost essentially proportional to the capacity (kW) of the proposed Facility.  Further, although no experience exists for this process [based on positive experience in other states, including California], it is expected that Facilities with capacity less than 100 kW will [shall] incur the minimum cost.  The process would be as follows:

- [Interconnection] Customer submits first the NOII form filled out properly and completely (perhaps with help from the Company [Interconnection Provider])

- [Interconnection] Customer then submits a simplified Application[, perhaps using the NYS document for units of 300 kVA or less,] filled out properly and completely with help from the Company [Interconnection Provider] as necessary.

- Company [Interconnection Provider] evaluates the Application, applies the screening methodology and verifies Facility equipment compliance with national standards and state certification (as appropriate).  Notice: The Company [Interconnection Provider] reserves the right to conduct additional studies if deemed necessary, such as but not limited to: protection review, aggregate harmonics analysis review, aggregate power factor review and voltage regulation review.[without additional cost beyond the initial application fee or additional time beyond the standard schedule.]

- Assuming all [the prescribed] screens are passed, Company [Interconnection Provider] notifies [Interconnection] Customer with approval for installation to proceed and the cost associated with the process.

- Company [Interconnection Provider] inspects completed installation for compliance with standards

- Assuming inspection is satisfactory, Company [Interconnection Provider] notifies [Interconnection] Customer that interconnection is allowed and submits required Interconnection Agreement (Exhibit 2) for [Interconnection] Customer signature

- Upon receipt of signed Agreement, Company [Interconnection Provider] notifies departments as shown in Figure 1.