Comparison of Existing and Proposed State and

Federal DG Interconnection Standards

a) DG Classification and Application Requirements

| Category | Mass Utility Proposal | Texas | New York | California | FERC ANOPR |
| --- | --- | --- | --- | --- | --- |
| DG Classification | 5 Levels: < 10 kW 10kW to 60kW 60kW to 300 kW 300kW to 1MW Above 1 MW | 2 Levels: < 300kW 300kW to 10MW Interconnection < 60kV | 1 Level: < 300 kW NYPSC Standardized Interconnection does not Address DG>300kW or Network DG | 2 Levels: Small – 11kVA or Less Larger – Above 11kVA More Stringent Protection Req’d for Larger Systems | 2 Levels: Small – Up to 2MW Large – Greater Than 2MW But Less Than 20MW |
| Application Fee | None Listed Interconnection Study Fees May Apply | None Listed Interconnection Study Fees May Apply | $350 Non-Refundable Applied to Cost of Interconnection No Fee for DG Rated <15kW | No Charge for Net Metered DG $800 All Others $600 Add’l for Supplemental Review $1400 Minimum if Customer Elects to Bypass Initial and Supplemental Review Steps | None Specified for Expedited Application $2000 to $50,000 for DG Rated 2MW to 20MW |
| Waiver of Application or Study Fee | Not Applicable | DG Pre-Certified Capacity Rating < 500kW Export Limited to 15% of Feeder Peak DG Contribution to Feeder Maximum Fault Current < 25% | Not Applicable | Net Metered DG 50% Credit if Customer Withdraws Application or if Rejected | Not Applicable |
| Capacity Threshold for Pre-Certification or Expedited Application | Capacity Rating of <10kW Required for Simplified Application. No Agreement Req’d | Capacity Rating < 500kW. No Study Fee Imposed, But Utility Still May Need to Upgrade System | Capacity Rating <15kVA Connected to Radial Systems Network Systems Not Addressed | Capacity Rating <11kVA Does Not Apply to Network Interconnections or for DG Exports | Up to 2MW |
| Minimum Threshold of DG System Impacts for Expedited Review | Radial - DG <5% of Line Segment Peak Load Network – DG <7% of Site Minimum Load Qualifies for Expedited Review | Minimum Threshold <500kW (Radial) <20kW (Network) | Full Review May Not be Needed if: DG<50kVA on 1Phase Line or <150kVA on Radial Feeder | Radial - DG <15% of Line Segment Peak Load | Radial – Aggregate DG May Not Exceed 15% of Circuit Peak or Design Capacity Network – 25% of Minimum Load Measured on Ckt Fault Current Contribution <25% of Max. |
| Maximum Time for Utility to Process Application | 45 Days Following Receipt of NOI | 4 Weeks for Pre-Certified DG 6 Weeks for Non-Certified DG | 3 Days to Issue Interconnection Agreement & 5 Days Once Application Received | 3 Days to Issue Interconnection Agreement & 10 Days Once Application Received | Not Specified – 15 Days for Limited Feasibility Study |
| Maximum Time for Utility to Perform System Review and/or Interconnection Study | 90 Days for QF’s and On-Site Generating Facilities (<60kW) No Specific Time Line provided for Non-QF’s >60kW | 4 Weeks-Radial Lines 6 Weeks-Network Systems | 4 Weeks if DG<15kVA 8 Weeks for Larger DG | 10 Days for Simplified Interconnection 20 Days for Supplemental Review Additional Time May be Needed for Interconnection Study | 15 Days for Limited Feasibility Study |
| Maximum Time Allowed for Utility to Interconnect DG to System | Not Specified | 4 Weeks After Receipt of Application for Pre-Certified DG 6 Weeks for Other DG Not Requiring System Upgrades 2 Weeks Following Utility Completion of System Upgrades | 14 Days Following On-Site Testing | Not Specified | Not Addressed |
| Credit for DG | Not Addressed | Utility Must Assess Benefits if Interconnection Study Identifies Need for Upgrades | Not Addressed | Not Addressed | Transmission Owner Should Apply Credits for Network Upgrades Paid by Customer |

b) Other Terms and Conditions; Procedures

| Category | Mass Utility Proposal | Texas | New York | California | FERC ANOPR |
| --- | --- | --- | --- | --- | --- |
| Utility Contact Assigned for DG? | Utility Assigns Account Manager Upon Receipt of NOI | Utility Contacts Are Listed in Appendix of Interconnection Manual | Utility Assigns Technical Staff as a Single Point of Contact | Utility Assigns Staff as a Single Point of Contact; Utility May Reassign | Not Addressed |
| Dispute Resolution Process? | None Indicated | Yes. PUCT Contact Informal or Formal Resolution w/in 20 Days for Informal Disputes; 35 Days for Formal | Yes Good Faith Resolution Up to 10 Days Mediation for up to 90 Days Referral to NYPSC if Not Resolved | Yes Parties Must Meet to Resolve 45 Days Following Applicant’s Written Dispute Unresolved Disputes are Forwarded to CPUC | Yes FERC’s alternative Dispute Resolution Process |
| Insurance Required? | Yes All DG<10KW and Net Metered DG <60kW Exempted | Not Addressed | No PSC Recommends Self Coverage | Yes Sliding Scale Requires Higher Coverage for Larger DG | Not Addressed |
| Distribution O&M Charge | None Specified | No, for distribution and transmission | None Specified | Customer Pays O&M For Facilities & Upgrades Used Solely for Interconnection | Not Addressed |

c) Other Facility Requirements

|  | Mass Utility Proposal | Texas | New York | California | FERC ANOPR |
| --- | --- | --- | --- | --- | --- |
| Visible Disconnect Required? | Yes, Except for DG < 10kW that Meets UL 1741 | Yes, with Flexibility as to Type of Disconnect Switch | Yes | Yes, Except for DG w/ Inverters Rated < 1kW (1kW Limit May be an Error) | Not Specifically Addressed. Must Meet Codes and Standards |
| Telecommunications Facilities Required? | Mandatory for DG > 5MW Remote Access of Meter Data for DG > 60kW Involving 3rd Party Sales | Mandatory for DG>2 MW | Not Addressed for DG<300 | 250kW for Interconnection <10kV 1MW for Systems Above >10kV | Not Addressed |
| Metering | Net Metering Up to 60kW Bi-Directional for DG Rated 60kW to 1000kW. Remote Access Req’d for Export Sales Bi-directional, Interval w/ Remote Access for DG>5MW; Telemetering Req’d Over 5MW | Case-by-Case Consistent with CPUC Metering Requirements | Case-by-Case Consistent with NYPSC Metering Requirements | Net Metering Allowed All Metering Must Comply w/ Utility Tariffs & Manuals | As Needed |
| Ongoing Verification and Periodic Testing | Protective Relay Test at Least Every 4 Years | Functional Test Required. Utility May Witness Tests Owner Must Maintain Logs of O&M, Which Utility May Inspect | Every 4 Years Annual for 1Phase Inverters <15kVA | Protection Tests Every 4 Years | Not Addressed |

d) Performance Criteria

|  | Mass Utility Proposal | Texas | New York | California | FERC ANOPR |
| --- | --- | --- | --- | --- | --- |
| Voltage Fluctuation (Time Allowed Within Range Prior to Auto-Disconnection) | IEEE 1547 Standard | +5% to –10% ( 30 Seconds) +10% to –30% ( 10 Cycles) | +5% to –10% ( 2 Seconds) <–50% ( 6 Cycles) | +10% to –12% ( Small DG) Less Than 60 volts ( 10 Cycles) 60 Volts-106 volts (2 Seconds) 132-165 volts (2 Seconds; 0.5 for DG>11KVA) Above 165 volts (6 Cycles) | Current National Standards and Codes Apply |
| Voltage Flicker | Meets IEEE 519 | 3% Voltage Drop Per IEEE 519 at PCC | Meets IEEE 519 | Meets IEEE 519 | Current National Standards and Codes Apply |
| Harmonics | IEEE Standard 519 | Follows IEEE Standard 519 5% THD @ 60 Hz 3% for Each Harmonic | Meets IEEE 519 | Meets IEEE 519 DG Will be Evaluated in Same Manner as Loads at DG Site | Current National Standards and Codes Apply |
| Frequency | -0.7Hz to +0.5 Hz Deviation from 60Hz Base | -0.7Hz to +0.5 Hz Deviation from 60Hz Base 15 Cycle Clearing Required for Deviations | -0.7Hz to +0.5 Hz Deviation from 60Hz Base (6 Cycles) | -0.7Hz to +0.5 Hz Deviation from 60Hz Base 10 Cycle Clearing Required for Deviations | Current National Standards and Codes Apply |
| Power Factor | Not Specified | Not Specified | 0.9 Leading or Lagging | 0.9 Leading or Lagging Acceptable | Not Addressed |
| Validation Tests | Company Maintains Right to Witness Tests – One Week Notice Required | 2 Week Notification Prior to Energization | No Time Frame Specified | No Time Frame Specified | Not Addressed |