Exhibit 3

INTERCONNECTION REQUIREMENTS DOCUMENT

CUSTOMER-OWNED GENERATING FACILITIES

(Revised 01/28/03, DGC Edits 02/03/03)

Protection Requirements For New or Modified Generation Interconnections with the Distribution System

E.3.1 General Requirements

Any Facility desiring to interconnect with the Company’s Distribution System or modify an existing interconnection must meet minimum specifications, where applicable, as set forth in the following documents and standards.  Additional requirements, including clarification of the specifications contained in these documents are outlined in Section _ (Process requirement for assigning Facilities under Simplified, Expedited or Standard Review paths) Sections E_ and E_ below (Protection Requirements for Group I and II Facilities).

- Institute of Electrical and Electronic Engineers (IEEE) Standard P1547, Draft 10 “Standard for Distributed Resources Interconnected with Electric Power Systems”.

- Underwriters Laboratories Inc. Standard UL 1741, November 1, 2002, “Inverters, Converters, andControllers for Use in Independent Power Systems”

- IEEE Standard 929-2000, “IEEE Recommended Practice for Utility Interface of Photovoltaic (PV) Systems”.

The specifications and requirements listed herein are intended solely to mitigate possible adverse impacts caused by the Facility on the Company’s equipment and on other customers of the Company.  They are not intended to address protection of the Facility itself or its internal load.  It is the responsibility of the Facility to comply with the requirements of all appropriate standards, codes, statutes and authorities to protect itself and its loads.

The Company shall not be responsible for the protection of the Facility’s facilities.  The Facility shall be responsible for protection of its system against possible damage resulting from parallel operation with the Company.  If requested by the Interconnecting Customer, the Company will provide system protection information for the line terminal(s) directly related to the interconnection.  This protection information contained herein is provided exclusively for use by the Interconnecting Customer in evaluating protection of the Facility’s facilities during parallel operation.

E.3.2 Facility Disconnection (Based on Language Contained in New York Requirements) [Note: Move entire section to appropriate Tariff location]

- .

E.3.3 Facility Classification

To determine the protection requirements for a given Facility, the following Groups have been established:

| Group | Maximum Capability (kW) |
| --- | --- |
| 1 | Facilities Qualified for Simplified Interconnection (< 10 kW) |
| 2 | All Facilities Not Qualified for Simplified Interconnection |

E.3.4 Net Metering

[Note: Move entire section to appropriate Tariff location]

### E.3.4 Protection Requirements

### Group 1 Facilities (Inverter-Based Facilities Up to 10kW)

- The inverter-based Facility shall be considered qualified if it meets requirements set for in Section _ (Process section describing requirements in Box 3 of Figure schematic)

- External Disconnect Switch:  For qualified inverters, a Company may choose not to require an external disconnect switch. Exception:  a Company may require an external disconnect switch at the point of common coupling with the Company or at another mutually agreeable point that is accessible to Company personnel at all times and that can be opened for isolation if the switch is required. The Company shall have the right to open this disconnect switch in accordance with Tariff Section __.

Group 2 Facilities

#### Requirements for Inverter-Based Facilities:

Group 2 inverter-based Facilities must meet the same protection criteria as specified in subsection (a) for Group 1 inverter-based Facilities.

#### Requirements for Induction and Synchronous Generator Facilities:

- The Facility shall provide a disconnect switch at the point of Generating Facility interconnection that can be opened for isolation.  The switch shall be in a location accessible to Company personnel at all times.  The switch shall be gang operated, have a visible break when open, be rated to interrupt the maximum generator output and be capable of being locked open, tagged and grounded on the Company side by Company personnel.  The visible break requirement can be met by opening the enclosure to observe the contact separation.  The switch shall be of a type generally accepted for use by the Company[??].    [Note: redundant to tariff text]  The Company shall exercise such right in accordance with Tariff Section ___E.3.2.

- An Interconnection Interrupting Device such as a circuit breaker or fused contactor shall be installed to isolate the Generating Facility from the Company’s system.  If there is more than one Interrupting Device,  this requirement applies  to each one individually.

- The Interconnecting Customer shall designate one or more Synchronizing Devices such as motorized breakers or contactor/breaker combinations to be used to synchronize the Facility’s generator to the Company’s system.  This "Synchronizing Device could be a device other than the Interrupting Device.  The Synchronizing Device(s) [Note: already covered in 1547 Section 4.1.8.3]must be capable of interrupting the current produced when the Facility is connected out of phase with the Company's system.

- The Company reserves the right to specify the winding connections for the transformer between the Company’s voltage and the Facility’s voltage (“Step Up Transformer”) as well as whether it is to be grounded or ungrounded at the Company's voltage.  In the event that the transformer winding connection is grounded-wye/grounded-wye the Company reserves the right to specify whether the generator stator is to be grounded or not grounded.  The Interconnecting Customer shall be responsible for procuring equipment with a level of insulation and fault withstand capability compatible with the specified grounding method. [NCI to suggest language to resolve grounding issue, including alternate methods to address grounding]

- A[Note: covered by 1547 clauses 4.1.3 and 4.3.2]

- or . [Note: This is redundant with the clause further down that begins with “Where protective relaying is required…”  which describes the situation better]

- [Note: The initial sentence is covered by 1547 Section 4.2 and the second sentence is better described in a clause below].

- . [Note: covered by 1547 references in Section 2 and 4.1.8.1&2]

- Voltage relays shall be frequency compensated to provide a uniform response in the range of 40 to 70Hz.

- Protective relays utilized by the Facility shall be sufficiently redundant and functionally separate so as to provide adequate protection,  consistent with Company practices and standards[??], upon the failure of any one component.  [NCI, DG Group and utilities to further review the applicability of this clause]

- The Company may require the Facility to be equipped with two independent, redundant relaying systems in accordance with NPCC criteria, where applicable, for the protection of the bulk power system if the interconnection is to the bulk power system or if it is determined that delayed clearing of faults within the Facility adversely affects the bulk power system

- A direct transfer tripping system, if one is required by either the Interconnecting Customer or by the Company, shall use equipment generally accepted for use by the Company and shall, at the option of the Company, use dual channels.

- Tripping by protective relays required to satisfy the protection requirements of this section must be hardwired to the device they are tripping.  No interposing computer or programmable logic controller or the like is permitted in the trip chain between the relay and the device being tripped unless authorized by the Company

- Where protective relays are required, their control circuits shall be DC powered from a UPS or have AC battery back [NCI to develop generic terminology].  Solid-state relays shall be self-powered,  DC powered from a station battery, or powered from a UPS.  If the Facility uses a non-latching interconnection contactor, AC powered relaying may be allowed provided the relay and its method of application is fail safe, meaning that if the relay fails or if the voltage and/or frequency of its AC power source deviate from the relay’s design requirements for power, the relay will immediately trip the generator by opening the coil circuit of the Interconnection Contactor.

- CT ratios and accuracy classes shall be chosen such that secondary current is less than 100 amperes and transformation errors are consistent with Company practices [??].

- The Facility shall be equipped with a direct voltage connection or a voltage transformer, connected to the Company side of the Interrupting Device.  The voltage from this VT shall be used in the interlock as specified in these requirements .  If the Facility’s step up transformer is ungrounded at the Company voltage, this VT shall be a single three-phase device or three single-phase devices connected from each phase to ground on the Company’s side of the Facility’s step up transformer, rated for phase-to-phase voltage and provided with two secondary windings.  One winding shall be connected in open delta, have a loading resistor to prevent ferroresonance, and be used for the relay specified in these requirements. [NCI to review applicability of this clause with utilities and DG group]

- On three phase installations when voltage relaying is required,  all three phases must be sensed either by three individual relays or by one relay that contains three elements.  If the voltage on any of the three phases is outside the bounds specified by the Company the unit shall be tripped.

- Interlock Transformer: If the Company’s study determines that this item is required, a voltage transformer shall be provided by the Facility and shall be connected to the Company side of the interconnecting breaker or contactor.  The voltage from this VT shall be used in the interlock as specified above.  For three phase applications, a VT for each phase is required.

- [Note: covered by both 1741 and 1547 Section 4.2.3]

- During system conditions where local area load exceeds system generation, NPCC Emergency Operation Criteria requires a program of phased automatic underfrequency load shedding of up to 25% of area load to assist in arresting frequency decay and to minimize the possibility of system collapse.  Depending on the point of connection of the Facility to the Company’s system and in conformance with the NPCC Emergency Operating Criteria, the Facility may be required to remain connected to the system during the frequency decline to allow the objectives of the automatic load shedding program to be achieved, or to otherwise provide compensatory load reduction, equivalent to the Facility’s generation lost to the system, if the Interconnecting Customer elects to disconnect the Facility at a higher underfrequency set point.  (:  NCI will assess applicability of NPCC rules at the distribution level with utilities)

- [Note: covered in Process Section Notes]

Additional Requirements for Induction Generator Facilities

a.	A Facility using induction generators connected in the vicinity of capacitance sufficient to self-excite the generator(s) shall meet the requirements for synchronous machines.  The capacitors that enable self-excitation may actually be external to the Facility.  The Company will not restrict its existing or future application of capacitors on its lines nor restrict their use by other customers of the Company to accommodate a Facility with induction machines.  As changes occur in the location and size of capacitors, the Facility may be required in the future to upgrade its interface to meet the requirements for synchronous machines if self-excitation becomes possible, even if not initially possible.

The Facility may be required to install capacitors to limit the adverse effects of drawing reactive power from the system for excitation of the generator.  Capacitors for supply of reactive power at or near the induction generator with a kVAR rating greater than 30% of the generator's kW rating may cause the generator to become self-excited.  (If self-excitation can occur, the Facility shall be required to provide protection as specified in  synchronous machine requirements.)

b.

]

- [Note: covered by 1547 Section 4.2.3]

Additional Requirements for Synchronous Generator  Facilities

a.

. [Note: covered by Process Section]

- The Interconnecting Customer is responsible for procuring any communications channels necessary between the Facility and the Company’s stations and for providing protection from transients and overvoltages at all ends of these communication channels.  The Interconnecting Customer will also bear the ongoing cost to lease these communication channels.

- If the Facility’s step up transformer connection is ungrounded, the Facility shall be equipped with a zero sequence overvoltage relay fed from the open delta of the three phase VT specified in this Protection Policy.

[Note: covered by both 1741 and 1547 Section 4.2.3]

- e	Note: redundent text to earlier section]

- The Facility may be required to use high-speed protection if time-delayed protection would result in degradation in the existing sensitivity or speed of the protection systems on the Company’s lines.

- The Facility may be required to be equipped to provide local breaker failure protection which may include direct transfer tripping to the Company's line terminal(s) in order to detect and clear faults within the Facility that cannot be detected by the Company's back-up protection.

h.	 [Note: redundent text to earlier section]

E.3.5    Protection System Testing and Maintenance (Ongoing IEEE work may address some of following the issues.  Further, it may be appropriate to include this section in a separate section of the Interconnection Agreement)

The Company shall have the right to witness the commissioning testing as defined in IEEE Std1547 Section 5.4 at the completion of construction and to receive a copy of all test data.   [Note: redundent to Table 1 Time Frames

- The Facility shall be equipped with whatever equipment is required to perform this test.  If a “simulated utility” is required to perform such testing the Company is unable to provide the equipment required to perform the test.

The protective relays shall be tested and maintained by the Interconnecting Customer on a periodic basis but not less than once every four years or as otherwise determined by the Company.  For relays installed in accordance with the NPCC Criteria for the Protection of the Bulk Power System, maintenance intervals shall be in accordance with such criteria.  The results of these tests shall be summarized by the Interconnecting Customer and reported in writing to the Company.

Inverters with field adjustable settings for their internal protective elements shall be periodically tested if those internal elements are being used by the Facility to satisfy these requirements.  If a simulated utility is required to perform such testing the Company is unable to provide the equipment required to perform the test.

In its sole discretion, the Company may waive all or some of these requirements.

E.3.6    Protection Requirements – Momentary Paralleling of Standby Generators (To be reviewed)

Protective relays to isolate the Facility for faults in the Company's system are not required if the paralleling operation is automatic and takes place for less than one-half of a second.

EXC: NU wants separate timer to ensure .5 second limit.

EXC: NU wants full complement of protective devices if time exceeds .5 seconds.

Parallel operation of the Facility with the Company’s system shall be prevented when the Company's line is dead or out of phase with the Facility.

The control scheme for automatic paralleling must be submitted by the Interconnecting Customer for review and acceptance by the Company prior to the Facility being allowed to interconnect with the Company’s system.

E.3.7	Protection System Changes (To be reviewed)

The Interconnecting Customer must provide the Company with reasonable advance notice of any proposed changes to be made to the protective relay system, relay settings, operating procedures or equipment that affect the interconnection.  The Company will determine if such proposed changes require re-acceptance of the interconnection per the requirements of this Protection Policy.

In the future, should the Company implement changes to the system to which the Facility is interconnected, the Interconnecting Customer will be responsible at its own expense for identifying and incorporating any necessary changes to its protection system.  These changes to the Facility’s protection system are subject to review and approval by the Company.

In its sole discretion, the Company may waive all or some of these requirements.