Excerpts from Joint Utilities Document (Figure 2 flow chart) and DG proposed screens (from their presentation)

Figure 2, Joint Utilities’ Proposed Interconnection Agreement

Slides 35 and 36 from DG Cluster’s Proposed Agreement

# Screens – Primary

## <5% of annual peak load on radial circuits

## <5% of peak load (or 50kW max) on spot networks (inverters only)

## Secondary grid distribution networks

### induction generator or inverter

### not exceeding 50% of facility minimum load

## <10% contribution to circuit max fault current

## Not cause grid protective devices to exceed 90% of their short circuit interrupting capability

## In aggregate, cannot be >10MW where transient stability limits posted

## Phase imbalance limits if single-phase and connected to center tap neutral of a 240V service

## <20kVA if single-phase and on a shared secondary

## Single-phase connection requirements

## <10% of line capacity if single phase and section configuration is three-phase, 4-wire or a mix

# Screens – Secondary

## Radial circuits: <15% of line section design capacity

## Spot networks: <5% of peak load on spot networks

## Secondary grid networks

### On any network, use reverse power protection except:

### if generator <50% of min facility load or 500kW

## Basically same limits on fault current contribution and short circuit interrupting impact as primary screen